## Calculation
FREE FLEX VENTING AND COMBUSTION AIR GUIDE
Venting pressure drop range: +0.30"wc max to -0.10"wc min
|  |  | Flue Gas Flow, ACFM |  |  | Combustion Air Requirements, ACFM
| Boiler Model | Flue Sizes | @ 40% Excess Air, 200°F |  |  | @ 40% Excess Air, 60°F
| FF-1000 | 6" | 301 |  |  | 220
| FF-1500 | 8" | 452 |  |  | 330
| FF-2000 | 8" | 603 |  |  | 441
| FF-2500 | 10" | 753 |  |  | 550
| FF-3000 | 10" | 904 |  |  | 661
** The combined pressure drop through the vent and combustion air duct shall not exceed 100 equivalent feet.
| VENTING |  |  |  |  | COMBUSTION AIR
FF-1000 | VENTING - PRESSURE DROP FACTOR |  |  |  |  | COMBUSTION AIR - PRESSURE DROP FACTOR
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM)
| 6 | 1 | 10 | 5 | 1534 | 6 | 0.6 | 6.25 | 3.13 | 1121
| 8 | 0.22 | 2.22 | 1.11 | 863 | 8 | 0.13 | 1.32 | 0.658 | 631
| VENTING - CALCULATED EQUIVALENT FEET |  |  |  |  | COMBUSTION AIR - CALCULATED EQUIVALENT FEET
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT)
| 6 |  |  |  | 0 | 6 |  |  |  | 0
| 8 |  |  |  | 0 | 8 |  |  |  | 0
[6 empty] | ** 6" Combined Venting & Combustion Air Duct | 0 eq/ft
[6 empty] | ** 8" Combined Venting & Combustion Air Duct | 0 eq/ft
FF-1500 | VENTING - PRESSURE DROP FACTOR |  |  |  |  | COMBUSTION AIR - PRESSURE DROP FACTOR
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM)
| 8 | 0.56 | 5.88 | 2.86 | 1296 | 8 | 0.3 | 3.03 | 1.49 | 946
| 10 | 0.174 | 1.75 | 0.87 | 829 | 10 | 0.09 | 0.92 | 0.46 | 605
| VENTING - CALCULATED EQUIVALENT FEET |  |  |  |  | COMBUSTION AIR - CALCULATED EQUIVALENT FEET
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT)
| 8 |  |  |  | 0 | 8 |  |  |  | 0
| 10 |  |  |  | 0 | 10 |  |  |  | 0
[6 empty] | ** 8" Combined Venting & Combustion Air Duct | 0 eq/ft
[6 empty] | ** 10" Combined Venting & Combustion Air Duct | 0 eq/ft
FF-2000 | VENTING - PRESSURE DROP FACTOR |  |  |  |  | COMBUSTION AIR - PRESSURE DROP FACTOR
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM)
| 8 | 1 | 10 | 5 | 1728 | 8 | 0.53 | 5.26 | 2.63 | 1264
| 10 | 0.31 | 3.125 | 1.56 | 1106 | 10 | 0.164 | 1.64 | 0.82 | 809
| 12 | 0.12 | 1.19 | 0.59 | 768 | 12 | 0.063 | 0.63 | 0.314 | 562
| VENTING - CALCULATED EQUIVALENT FEET |  |  |  |  | COMBUSTION AIR - CALCULATED EQUIVALENT FEET
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT)
| 8 |  |  |  | 0 | 8 |  |  |  | 0
| 10 |  |  |  | 0 | 10 |  |  |  | 0
| 12 |  |  |  | 0 | 12 |  |  |  | 0
[6 empty] | ** 8" Combined Venting & Combustion Air Duct | 0 eq/ft
[6 empty] | ** 10" Combined Venting & Combustion Air Duct | 0 eq/ft
[6 empty] | ** 12" Combined Venting & Combustion Air Duct | 0 eq/ft
FF-2500 | VENTING - PRESSURE DROP FACTOR |  |  |  |  | COMBUSTION AIR - PRESSURE DROP FACTOR
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM)
| 8 | 1.53 | 16.67 | 8.33 | 2158 | 8 | 0.83 | 8.3 | 4.17 | 1576
| 10 | 0.478 | 5 | 2.44 | 1381 | 10 | 0.26 | 2.56 | 1.28 | 1009
| 12 | 0.183 | 1.852 | 0.92 | 959 | 12 | 0.1 | 0.98 | 0.49 | 701
| VENTING - CALCULATED EQUIVALENT FEET |  |  |  |  | COMBUSTION AIR - CALCULATED EQUIVALENT FEET
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT)
| 8 |  |  |  | 0 | 8 |  |  |  | 0
| 10 |  |  |  | 0 | 10 |  |  |  | 0
| 12 |  |  |  | 0 | 12 |  |  |  | 0
[6 empty] | ** 8" Combined Venting & Combustion Air Duct | 0 eq/ft
[6 empty] | ** 10" Combined Venting & Combustion Air Duct | 0 eq/ft
[6 empty] | ** 12" Combined Venting & Combustion Air Duct | 0 eq/ft
FF-3000 | VENTING - PRESSURE DROP FACTOR |  |  |  |  | COMBUSTION AIR - PRESSURE DROP FACTOR
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM)
| 8 | 2.22 | 25 | 11.11 | 2591 | 8 | 1.19 | 12.5 | 5.9 | 1895
| 10 | 0.68 | 7.14 | 3.57 | 1650 | 10 | 0.37 | 3.7 | 1.85 | 1213
| 12 | 0.267 | 2.7 | 1.35 | 1152 | 12 | 0.14 | 1.41 | 0.7 | 842
| VENTING - CALCULATED EQUIVALENT FEET |  |  |  |  | COMBUSTION AIR - CALCULATED EQUIVALENT FEET
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT)
| 8 |  |  |  | 0 | 8 |  |  |  | 0
| 10 |  |  |  | 0 | 10 |  |  |  | 0
| 12 |  |  |  | 0 | 12 |  |  |  | 0
[6 empty] | ** 8" Combined Venting & Combustion Air Duct | 0 eq/ft
[6 empty] | ** 10" Combined Venting & Combustion Air Duct | 0 eq/ft
[6 empty] | ** 12" Combined Venting & Combustion Air Duct | 0 eq/ft

## Calculation old (hidden)
ARCTIC VENTING AND COMBUSTION AIR TABLES
Venting pressure drop range: +0.30"wc max to -0.10"wc min
|  |  | Flue Gas Flow, ACFM |  |  | Combustion Air Requirements, ACFM
| Boiler Model | Flue Sizes | @ 40% Excess Air 200°F |  |  | @ 40% Excess Air 60°F
| ARC-1000 | 6" | 301 |  |  | 220
| ARC-1500 | 8" | 452 |  |  | 330
| ARC-2000 | 8" | 603 |  |  | 441
| ARC-2500 | 10" | 753 |  |  | 550
| ARC-3000 | 10" | 904 |  |  | 661
| PRESSURE DROP FACTORS |  |  |  |  | EQUIVALENT FEET CALCULATION
** The combined pressure drop through the vent and combustion air duct shall not exceed 100 equivalent feet.
ARC-1000 | VENTING |  |  |  |  | VENTING
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 6 | 1 | 10 | 5 | 1534 | 6 |  |  |  | 0 | 100
| 8 | 0.22 | 2.22 | 1.11 | 863 | 8 |  |  |  | 0 | 454.5455
| COMBUSTION AIR DUCT |  |  |  |  | COMBUSTION AIR DUCT
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 6 | 0.6 | 6.25 | 3.13 | 1121 | 6 |  |  |  | 0 | 166.6667
| 8 | 0.13 | 1.32 | 0.658 | 631 | 8 |  |  |  | 0 | 769.2308
[9 empty] | ** 6" Combined Venting & Combustion Air Duct | 0
[9 empty] | ** 8" Combined Venting & Combustion Air Duct | 0
ARC-1500 | VENTING |  |  |  |  | VENTING
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 8 | 0.56 | 5.88 | 2.86 | 1296 | 8 |  |  |  | 0 | 178.5714
| 10 | 0.174 | 1.75 | 0.87 | 829 | 10 |  |  |  | 0 | 574.7126
| COMBUSTION AIR DUCT |  |  |  |  | COMBUSTION AIR DUCT
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 8 | 0.3 | 3.03 | 1.49 | 946 | 8 |  |  |  | 0 | 333.3333
| 10 | 0.09 | 0.92 | 0.46 | 605 | 10 |  |  |  | 0 | 1111.1111
[9 empty] | ** 8" Combined Venting & Combustion Air Duct | 0
[9 empty] | ** 10" Combined Venting & Combustion Air Duct | 0
ARC-2000 | VENTING |  |  |  |  | VENTING
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 8 | 1 | 10 | 5 | 1728 | 8 |  |  |  | 0 | 100
| 10 | 0.31 | 3.125 | 1.56 | 1106 | 10 |  |  |  | 0 | 322.5806
| 12 | 0.12 | 1.19 | 0.59 | 768 | 12 |  |  |  | 0 | 833.3333
| COMBUSTION AIR DUCT |  |  |  |  | COMBUSTION AIR DUCT
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 8 | 0.53 | 5.26 | 2.63 | 1264 | 8 |  |  |  | 0 | 188.6792
| 10 | 0.164 | 1.64 | 0.82 | 809 | 10 |  |  |  | 0 | 609.7561
| 12 | 0.063 | 0.63 | 0.314 | 562 | 12 |  |  |  | 0 | 1587.3016
[9 empty] | ** 8" Combined Venting & Combustion Air Duct | 0
[9 empty] | ** 10" Combined Venting & Combustion Air Duct | 0
[9 empty] | ** 12" Combined Venting & Combustion Air Duct | 0
ARC-2500 | VENTING |  |  |  |  | VENTING
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 8 | 1.53 | 16.67 | 8.33 | 2158 | 8 |  |  |  | 0 | 65.3595
| 10 | 0.478 | 5 | 2.44 | 1381 | 10 |  |  |  | 0 | 209.205
| 12 | 0.183 | 1.852 | 0.92 | 959 | 12 |  |  |  | 0 | 546.4481
| COMBUSTION AIR DUCT |  |  |  |  | COMBUSTION AIR DUCT
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 8 | 0.83 | 8.3 | 4.17 | 1576 | 8 |  |  |  | 0 | 120.4819
| 10 | 0.26 | 2.56 | 1.28 | 1009 | 10 |  |  |  | 0 | 384.6154
| 12 | 0.1 | 0.98 | 0.49 | 701 | 12 |  |  |  | 0 | 1000
[9 empty] | ** 8" Combined Venting & Combustion Air Duct | 0
[9 empty] | ** 10" Combined Venting & Combustion Air Duct | 0
[9 empty] | ** 12" Combined Venting & Combustion Air Duct | 0
ARC-3000 | VENTING |  |  |  |  | VENTING
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 8 | 2.22 | 25 | 11.11 | 2591 | 8 |  |  |  | 0 | 45.045
| 10 | 0.68 | 7.14 | 3.57 | 1650 | 10 |  |  |  | 0 | 147.0588
| 12 | 0.267 | 2.7 | 1.35 | 1152 | 12 |  |  |  | 0 | 374.5318
| COMBUSTION AIR DUCT |  |  |  |  | COMBUSTION AIR DUCT
| FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | VELOCITY | FLUE VENT | STRAIGHT LENGTH | 90° ELBOW | 45° ELBOW | TOTAL
| DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (FPM) | DIA (Inches) | (EQ.FT/FT) | (EQ.FT) | (EQ.FT | (EQ.FT) | Max Feet
| 8 | 1.19 | 12.5 | 5.9 | 1895 | 8 |  |  |  | 0 | 84.0336
| 10 | 0.37 | 3.7 | 1.85 | 1213 | 10 |  |  |  | 0 | 270.2703
| 12 | 0.14 | 1.41 | 0.7 | 842 | 12 |  |  |  | 0 | 714.2857
[9 empty] | ** 8" Combined Venting & Combustion Air Duct | 0
[9 empty] | ** 10" Combined Venting & Combustion Air Duct | 0
[9 empty] | ** 12" Combined Venting & Combustion Air Duct | 0